## Thermal Expansion sizing
To properly size an expansion tank, it is necessary to calculate the total system volume.
To begin, determine the pipe lengths of each diameter of pipe used on the project and enter the lengths on page 2 "Linial ft of piping".
3 options are automatically given which include copper tube type L, Schedule 40 Steel pipe, Schedule 80 Steel pipe.
Also on page 2, enter the volume of the water storage vessel and boiler.
Enter the design water temperature from the dropdown menu
Enter the minimum water temperature **, typically 90 degrees F.
Enter the supply water pressure
Maximum system pressures are given at 100 psig, 110 psig and 120 psig
Select a tank larger than the Mimium Tank Volume and the Expansion volume
** During the initial start-up, this will be well below 90 degrees F.
|  |  | Copper Tube ( Type L) | Steel Pipe (Sch 40) | Steel Pipe (Sch 80)
1 | Total System Water Volume (from next page) | Gallons | 0 | 0 | 0
Expansion Factor
2 | Design Water Temp | 180 | 0.02358
3 | Minimum water temperature (typ 90 F) | 90
4 | Supply water pressure | 70
6 | Maximum pressure |  | 100 psig | 110 psig | 120 psig
7 | Acceptance Factor |  | 0.261 | 0.321 | 0.371
8 | Minimum Tank Volume |  | 0 | 0 | 0
9 | Expansion volume |  | 0 | 0 | 0

## Linial ft of piping
Volume (gallons) of water in piping
Project Pipe Length
Pipe Size | [15 empty] | Storage tank Volume | Boiler Volume
Steel Pipe (Sch 80) | 0.0122 | 0.0277 | 0.0374 | 0.0666 | 0.0918 | 0.1534 | 0.2435 | 0.3413 | 0.4617 | 0.5972 | 0.9449 | 1.3541 | 2.3721 | 3.7304 | 5.2782
Steel Pipr (Sch 40) | 0.0158 | 0.0277 | 0.0499 | 0.0777 | 0.1058 | 0.1743 | 0.2487 | 0.384 | 0.5136 | 0.6613 | 1.0391 | 1.5008 | 2.5988 | 4.0963 | 5.8146
Copper Tube ( Type L) | 0.0121 | 0.0251 | 0.0429 | 0.0655 | 0.0925 | 0.161 | 0.248 | 0.354 | 0.478 | 0.571 | 0.971 | 1.39 | 2.44 | 3.78 | 5.45
Pipe Size | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | 8" | 10" | 12" |  |  | Total System Gallons
Steel Pipe (Sch 80) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Steel Pipe (Sch 80)
Steel Pipr (Sch 40) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Steel Pipr (Sch 40)
Copper Tube ( Type L) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Copper Tube ( Type L)